## Drain flow calc
Photo Montage Reference 2025_1_9_T1295094_007_IMG_8477_3290855
Metadata says taken 30/12/2024 7:47am, which is before Bayview Rd burst was found
Survey of pit undertaken by Andrew Gordon on 5 March 2025 to establish diameter of pipe.
| surveyed | photo | photo scale | by scaling
Pipe diameter | 0.6 | 38.44 | 64.0667
Water width |  | 16.08 |  | 0.25099 | m
water width = chord legnth
L = 2 x sqrt(r2-d2)
L/2 = sqrt(r2-d2)
(L/2)^2 = r^2-d^2
d^2=R^2-(L/2)^2
d=sqrt(R^2-(L/2)^2)
d, height = | 0.27249
depth of water (r-d) | 0.027509
Council have not provided stormwater drain information, so need to estimate
Distances measured using GT Viewer (image beside)
9.5m beween Pit A and Pit B
Surface at Pit A from site survey is 53.9m
Surface at Pit B is 54.7 from contours
Surface gradient | 0.084211 |  | 1 in | 11.875
Grade next pit upstream of pit B
54.7 | (surface level at pit B)
58.9 | (surface level at pit upstream of pit B)
49.8m apart
Surface gradient | 0.084337 |  | 1 in | 11.8571
Council have now provided some data, but has some issues including pipe position and diameters seem incorrect
Council data says Pit A is 3m deep and Pit B is 1.6m deep
From survey of Pit A, we know the pipe between Pit A and Pit B is 1.81m deep at Pit A
From survey, IL of pipe between Pit A and Pit B at Pit A is |  |  |  |  | 52.09
Assumed IL at Pit B is 54.7 -1.6 |  |  | 53.1
Pipe grade is | 0.10632 |  | 1 in | 9.4059
19/6/2025. Additional survey undertaken of Pit B on 18/6/2025
From 5/3/2025 pit A invert level is |  |  | 52.09
From 18/6/2025, pit B invert level is |  |  | 53.03
From 18/6/2025, distance between pit Ils is |  |  | 8.77
Pipe grade is | 0.10718 |  | 1 in | 9.3298
Calculate flow using Colebrook White calculator
k =0.6mm, u=1.14E-06, D=0.6m
For pipe grade 1 in 11.9 |  | partial flow is 8.2L/s
For pipe grade 1 in 9.4 |  | partial flow is 9.2 L/s
For pipe grade 1 in 9.3 |  | partial flow is 9.3 L/s
These calculations provide an indication of flow in pipe, however are based on approximate values
Sensitivity results show plausible values range from 7.3L/s to 12.1L/s with only one variable at a time changed. It is likely that multiple variables are inaccurate, which would give a wider range of values
Peak flow calculated by Jonathan Crook is 1.35ML/d or 15.6L/s
`

## Senstivity results
Vary one parameter at a time, to see affect
Pipe ID | Grade | Dia Length | Water width | Depth of water | Flow
0.6 | 9.4 | 38.44 | 16.08 | 0.027509 | 9.2 | Humes Class 2 current day is 0.61m internal diameter
0.61 | 9.4 | 38.44 | 16.08 | 0.027968 | 9.6 | Humes class 3 current day is 0.6m internal diameter
0.62 | 9.4 | 38.44 | 16.08 | 0.028426 | 10 | Humes class 4 current day is 0.586m internal diameter
0.675 | 9.4 | 38.44 | 16.08 | 0.030948 | 12.1
0.6 | 9.4 | 38.44 | 16.08 | 0.027509 | 9.2
0.6 | 9.4 | 40 | 16.08 | 0.025308 | 7.7
0.6 | 9.4 | 37 | 16.08 | 0.029812 | 10.9
0.6 | 9.4 | 38.44 | 16.08 | 0.027509 | 9.2
0.6 | 9.4 | 38.44 | 17 | 0.030932 | 11.8
0.6 | 9.4 | 38.44 | 15 | 0.023783 | 6.7